## Slide 1: PID tuning using the SIMC rule
Sigurd Skogestad

## Slide 2: Lecture outline
SIMC rule for first order systems
Closed loop tuning
Half-rule for higher order models

## Slide 3: PID controller
Time domain ("ideal" PID)
Laplace domain ("ideal"/"parallel" form)
Usually . Only two parameters left ( and )…
How difficult can it be?
  Surprisingly difficult without systematic approach!

## Slide 4: PID tuning – wikipedia
https://en.wikipedia.org/wiki/PID_controller#Loop_tuning
Hm…. SIMC tuning is not mentioned – maybe someone can update wiki
SIMC Has tuning parameter, analytically derived, works also on The process must not be
delay processes(where ZN does not work) oscillatory
BAD
method
No, less agressive
Version of ZN
??

## Slide 5: Trans. ASME, 64, 759-768 (Nov. 1942).
Disadvantages Ziegler-Nichols:
Aggressive settings
No tuning parameter
Poor for processes with large time delay ()
Comment:
Similar to SIMC for integrating process with c=0 (aggressive!):
Kc = 1/k’ 1/
I = 4

## Slide 7
Disadvantage IMC-PID (=Lambda tuning):
Many rules
Poor disturbance response for «slow» processes (with large 1/)

## Slide 10
1
(gives Gain Margin>3)
Only one tuning parameter:
Closed-loop time constant:
k’=k/τ1
+ Filter time constant,
Summary SIMC PID tuning rule
With anti windup

## Slide 11: SIMC PI tuning rule
Approximate process as first-order with delay (e.g., use “half rule”)
    k = process gain
    = process time constant
    = process delay
Derive SIMC tuning rule*:
S. Skogestad, “Simple analytic rules for model reduction and PID controller design”, J.Proc.Control, Vol. 13, 291-309, 2003
(*) “Probably the best simple PID tuning rules in the world”
: Desired closed-loop response time (tuning parameter)
Open-loop step response
Integral time rule combines well-known rules:
IMC (Lambda-tuning): Same as SIMC for small ()
Ziegler-Nichols: Similar to SIMC for large (if we choose ; aggressive!)

## Slide 12: Derivation of SIMC-PID tuning rules
PI-controller (based on first-order model)
For second-order model add D-action.
  For our purposes, simplest with the “series” (cascade) PID-form:

## Slide 13: Basis: Direct synthesis (IMC)
Closed-loop response to setpoint change:
Idea: specify desired response and from this get the controller:
Notes: Go to blackboard at this point!

## Slide 14
SIMC-tunings
NOTE: Setting the steady-state gain = 1 in T will result in integral action in the controller!
Time delay is not really desired
but it cannot be avoided

## Slide 15: IMC Tuning = Direct Synthesis
Algebra:
SIMC-tunings
Surprisingly, this PID-controller is generally better, or at least more robust with respect to changes in the time delay θ, than the Smith Predictor controller from which it was derived. We are lucky .
Reference: Chriss Grimholt and Sigurd Skogestad. ''Should we forget the Smith Predictor?'' (2018) In 3rd IFAC conference on Advances in PID control, Ghent, Belgium, 9-11 May 2018. In IFAC papers Online (2018) .
IMC-tuning is the same as “Lambda-tuning”: c is sometimes called λ

## Slide 16: Example step setpoint response (with choice τc=θ =2)
s=tf(‘s’);
k=1; tau=10; theta=2;
g = k*exp(-theta*s)/(tau*s+1);
tauc=theta;
Kc=(1/k)*(tau/(tauc+theta)); % Kc=2.5
taui=tau;
c = Kc*(1+ 1/(taui*s));
T = g*c/(1+g*c);
Tideal = exp(-theta*s)/(tauc*s+1);
step(T,Tideal,20)
y (PI)
Red: «ideal» = «originally desired» (with Smith Predictor)
PI: Overshoot (y=1.04) is from approximation exp(-θs) 1 - θs

## Slide 17: Input usage for setpoint response
%Input usage
figure(2);
KS = c/(1+g*c);
KSideal = (1/k)*(tau*s+1)/(tauc*s+1);
step(KS,KSideal,20);
axis([0 20 0 5])
u (PI)
Red: «ideal» (with Smith Predictor)
The process has a «natural» time constant τ=10, and we use control to «speed it up» to τc=2.
This is why we get an overshoot for the input
(for PI-control, u starts at 0, jumps up to Kc=2.5 and then I-action increases it to 3 at its peak, before settling at its steady-state value of 1).

## Slide 18
Integral time
Found: Integral time = dominant time constant (I = 1)
Gives P-controller for integrating process (I = ∞)
  This works well for setpoint changes
  But: I needs to be modified (reduced) for integrating disturbances
  Example. “Almost-integrating process” with disturbance at input:
  G(s) = e-s/(30s+1)
    Original integral time I = 30 gives poor disturbance response
    Try reducing it!
g
c
d
y
u

## Slide 19: Effect of decreasing
SIMC
SIMC modification:
Decrease integral time to improve disturbance rejection
for slow processes (with large τ)!

## Slide 20: Conclusion: SIMC-PID Tuning Rules
One tuning parameter: c

## Slide 21
Some special cases
One tuning parameter: c
(1)(*) Note that we get pure I-controller for static process with delay.

## Slide 22: Selection of tuning parameter c
Two main cases
TIGHT CONTRO L: Want “fastest possible control” subject to having good robustness
    Want tight control of active constraints (“squeeze and shift”)
SMOOTH CONTROL: Want “slowest possible control” subject to acceptable disturbance rejection
    Prefer smooth control if fast control is not required
TIGHT CONTROL (τc small):
SMOOTH CONTROL (τc large):

## Slide 23
TIGHT CONTROL
1/Ms

## Slide 24
Typical closed-loop SIMC responses with the choice c=
TIGHT CONTROL

## Slide 25
Example 2. Compare PI and PID
s=tf('s')
g=(-0.3*s+1)*(0.08*s+1)/((2*s+1)*(s+1)*(0.4*s+1)*(0.2*s+1)*(0.05*s+1)^3)
k=1;
tau1=2.5, tau2=0, theta=1.47, tauc=theta % 1st order
%tau1=2, tau2=1.2, theta=0.77, tauc=theta % 2nd order
Kc=(1/k)*tau1/(tauc+theta) % Kc. PI: 0.85 PID: 1.30
taui=min(tau1,4*(tauc+theta)) % taui. PI: 2.50 PID: 2
taud=tau2; % taud. PI: 0 PID: 1.2
cpi=Kc*(1+1/(taui*s));
cd=(taud*s+1)/(0.1*taud*s+1);
cpid=cpi*cd;
L = cpid*g
S=inv(1+L)
%setpoint response
Ty=g*cpi*S, Ty=minreal(Ty); % without D-action on setpoint
Tuy=cpi*S, Tuy=minreal(Tuy); % without D-action on setpoint
%Input disturbance
gd=g;
Td=gd*S; Td=minreal(Td);
Tud=-gd*cpid*S; Tud=minreal(Tud);
Typi=Ty; Tdpi=Td; Tuypi=Tuy; Tudpi=Tud;
%Typid=Ty; Tdpid=Td; Tuypid=Tuy; Tudpid=Tud;
figure(1),step(Typi,'blue',Typid,'blue--',Tuypi,'red',Tuypid,'red--',15)
figure(2),step(Tdpi,'blue',Tdpid,'blue--',Tudpi,'red',Tudpid,'red--',15)
TIGHT CONTROL
Note: tau2>theta , so 2nd order and PID gives
perfromance improvement compared to PI

## Slide 26
Comparison of
PI and PID - -
Input u
Input u
STEP SETPOINT CHANGE (ys)
(note: without D-action on setpoint,
so u jumps initially to Kc also for PID)
STEP INPUT DISTURBANCE (gd=g)
PI
PID
Output y
Output y
Conclusion:
PID is quite a lot better.
(expected since tau2=1.2
> theta=0.77)
Example 2.
PI
PID
PID
PI
PI
PID

## Slide 27
Conclusion D-action (for series-form PID):
1. Use PID with D = 2 for dominant 2nd order processes with 2 >θ (otherwise, add 2/2 to effective delay θ and use PI)
2. Use derivative action (PID) for unstable processes, for example, a double integrating process (not so common in process control).
3. Derivative action (PID) can help a little to speed up response for a process with time delay (e.g. use D = θ/3), but we then need to reduce C (i.e., increase Kc) to get the performance benefit (e.g., reduce C from θ to θ/2).
We did not do this in the above simulation, so this is why the benefit of D-action is small.
Example 3 (next slide): Compare SIMC-PI with PID with D = θ/3 using C = θ (red curve, small benefit) and C = θ/2 (yellow curve, less overshoot).
4. If you end up using a “large” c, such that you have c > 2D (approximately), then D-action is not helping much and you may consider PI-control instead. Example: See above simulation which has c= θ and D= θ/2, that is, c = 2D.
SIMC-tunings

## Slide 28
Example 3 (disturbance response Dynea reactor):
(1) Effect of wrong tau-I, (2) Use of tau-D to reduce overshoot
Note: Often D-action requires much more input usage - but in this example the input usage (not shown) is almost the same for all controllers. This is because the disturbance is so «slow» (almost integrating)

## Slide 29
Too complicated

## Slide 30: SIMC: Tuning parameter (τc) correlates nicely with robustness measures. GM and DM increase linearly with τc
Ms
GM
PM
c /
c /
DM=
D / =
PM/ωc
3
1
2
1.6
1
60o
1/Ms

## Slide 31: When do we need «tight control»? For hard constraints
«SQEEZE and SHIFT» RULE
Original
tuning
Improved
tuning
Optimized
operation
Setpoint
Squeeze
Shift
time

## Slide 32: Tuning for smooth control
SMOOTH CONTROL
Tuning parameter: c = desired closed-loop response time
Selecting c= if we need “tight control” of y.
Other cases: “Smooth control” of y is sufficient, so select c >  for
  slower control
  smoother input usage
    less disturbing effect on rest of the plant
  less sensitivity to measurement noise
  better robustness
Question: Given that we require some disturbance rejection.
  What is the largest possible value for c ?
  ANSWER: c,max =1/ωd (where ωd is defined as the frequence where |gd(jωd)| = ymax/dmax )
Proof. y=Sgd d, where S=(1+L). Require |y|<ymax at all frequencies, so |S| < |gd| d/ymax at all frequencies.
The integral action takes care of most of the disturbance rejection, so usually, the «worst-case» frequency is where |S| reaches 1, which is approximately at wc=1/tauc.
So define wd as the frequency where (gd/g) d/ymax = 1 and we must require wc > wd or equivalently tauc < 1/wd. Thus we have tauc.maxc=1(wd.
This bound may be optimistic if there are disturbances with two or more «slow» poles, because then the worst-case frequency may be lower than wc.
Comment: An simpler (but sometimes conservative) answer is to select Kc,min =|ud|/|ymax| where |ud| is the input magnitude to reject the maximum disturbance. (Given Kc,min we may obtain the corresponding tauc,max using the SIMC-rule for Kc).
.
More detailed proof: S. Skogestad, ``Tuning for smooth PID control with acceptable disturbance rejection'', Ind.Eng.Chem.Res, 45 (23), 7817-7822 (2006).

## Slide 33: Conclusion PID tuning
3. Derivative time: Use for dominant second-order processes (τD= τ2) … and
in rare cases to speed up the response with time delay (τD= θ/3).
ud= input change required to reject disturbance
ymax = largest allowed output change
|ud|

## Slide 34: Level control
Level control often causes problems
Typical story:
  Level loop starts oscillating
  Operator detunes by decreasing controller gain
  Level loop oscillates even more
  ......
???
Explanation: Level is by itself unstable and requires control.
LEVEL CONTROL

## Slide 35: Level control: Can have both fast and slow oscillations
Slow oscillations (Kc too low): P > π τI
Fast oscillations (Kc too high): P < π τI
Fast oscillations: Caused by (effective) time delay
Here: Consider the common slow oscillations
LEVEL CONTROL
P=period of oscillations = 2π/ω

## Slide 36: How avoid slowly oscillating levels?
LEVEL CONTROL
0.1 ¼ 1/2

## Slide 37: Case study oscillating level
We were called upon to solve a problem with oscillations in a distillation column
Closer analysis: Problem was oscillating reboiler level in upstream column
Use of Sigurd’s rule solved the problem
LEVEL CONTROL

## Slide 38
LEVEL CONTROL

## Slide 39: Need a model for tuning
Model: Dynamic effect of change in input u (MV) on output y (CV)
First-order + delay model for PI-control
Second-order model for PID-control
  Recommend: Use second-order model only if

## Slide 40: 1. Step response experiment
Make step change in one u (MV) at a time
Record the output (s) y (CV)

## Slide 41: 1A. Open-loop setting
STEP IN INPUT u
RESULTING OUTPUT y
: Delay - Time where output does not change
1: Time constant - Additional time to reach
63% of final change
k =  y(∞)/ u : Steady-state gain
Δy(∞)
Δu

## Slide 42: Step response of integrating process
Δy
Δt
Imagine this as a 1st order with "infinite" :

## Slide 43: 1B. Closed-loop setpoint response
Shams’ method: P-controller with about 20-40% overshoot
Kc0=1.5
Δys=1
Δyu=0.54
Δyp=0.79
tp=4.4
OBTAIN 5 DATA IN RED (wait for first overshoot
and undershoot), and then read off:
tp=4.4, dyp=0.79; dyu=0.54, Kc0=1.5, dys=1
dyinf = 0.45*(dyp + dyu)
Mo =(dyp -dyinf)/dyinf % Mo=overshoot (about 0.3)
b=dyinf/dys
A = 1.152*Mo^2 - 1.607*Mo + 1.0
r = 2*A*abs(b/(1-b))
%2. OBTAIN FIRST-ORDER MODEL:
k = (1/Kc0) * abs(b/(1-b))
theta = tp*[0.309 + 0.209*exp(-0.61*r)]
tau = theta*r
3. CAN THEN USE SIMC PI-rule
Example 2: Get k=0.99, theta =1.68, tau=3.03
Ref: Shamssuzzoha and Skogestad (JPC, 2010)
+ modification by C. Grimholt (Project, NTNU, 2010; see also PID-book 2012,
Sigurd Skogestad and Chriss Grimholt. ''The SIMC Method for Smooth PID Controller Tuning'' (2012))
Δy∞

## Slide 44: 2. Model reduction
Start with complicated stable model on the form
Want to get a simplified model on the form
Most important parameter is the “effective” delay

## Slide 45
Details:

## Slide 46: Example 1
Half rule

## Slide 47
s=tf('s')
g=(-0.1*s+1)/[(5*s+1)*(3*s+1)*(0.5*s+1)]
g1 = exp(-2.1*s)/(6.5*s+1)
g2 = exp(-0.35*s)/[(5*s+1)*(3.25*s+1)]
step(g,g1,g2)
0
5
10
15
20
25
30
35
40
-0.2
0
0.2
0.4
0.6
0.8
1
Step Response
Time (seconds)
Amplitude
0
0.5
1
1.5
2
2.5
3
3.5
4
4.5
5
-0.05
0
0.05
0.1
0.15
0.2
0.25
0.3
0.35
0.4
Step Response
Time (seconds)
Amplitude
Example 2
Original (third-order with inverse response)
First-order approx. using half rule
Second-order approx. using half rule

## Slide 48
half rule
3
MODEL, Approach 2
Comment: The subtraction of T0=0.08 from the effective delay follows from the approximation (0.08s+1)/(0.2s+1) (rule T3).
Alternatively, we could have used the approximation (0.08s+1)/(0.05s+1) (rule T1b) which would reduce the effective delay by 0.05 (instead of 0.08). In any case, it only has a small effect om the effective delay, so it does not matter much for the final result.

## Slide 49
half rule
3
MODEL, Approach 2

## Slide 50
g0: Original complicated system
(with 2 zeros and 8 poles)
g2: 2nd order with delay (half rule, θ=0.77)
g1: 1st order with delay (half rule, θ=1.47)
Example 3.

## Slide 51: Example 4. Integrating process
Example. g0 = 5/(s*(3*s+1)),
g = 5*exp(-1.5*s)/s,
step(g,g0,10)
Doesn’t look so good
But it’s OK

## Slide 52: Higher-order example
Original 7th order, g0
1st-order, half rule, g1
2nd-order, half rule, g2
1st-order, closed loop, gcl

## Slide 53: Approximation of LHP-zeros
τc = desired closed-loop time constant
We should approximate T0 by a “close-by” 0 .
BUT: The goal is to use the model for control purposes, so we would like to keep (i.e., not approximate) the  which is closest to the desired c.
In Example E3, we have two possible values for 0 , namely 20 and 1. Since T0=15, it seems clear that we should select the closest 0 = 20 and use rule T2.
But what if T0=2, maybe selecting 0 = 1 is better (and using rule T1)?
No, this is not clear. Since c is between 0.05 (PID) and 0.15 (PI), we may want to keep  =1 which is closest to c ,that is, also in this case select 0 = 20 (and use rule T2)
This may seem surprising, but it turns out that it will not matter very much in the case for the PI/PID-tunings (try!), because k/tau1 (and thus Kc) will not change much and because tauI = min(tau,4(tauc+theta)).
Of course, if T0 gets much closer to 1, then we should select 0 = 1.
Generally, the LHP-zeros approximation rules results in acceptable (robust) PI/PID-settings, but not necessarily the “optimal” settings.
g0
g2
g1
PID-controller (from 2nd order model) will give performance improvement because τ2 > θ

## Slide 54: Step response (without control)
g0 = 2*(15*s+1)/((20*s+1)*(s+1)*(0.1*s+1)^2)
g1=1.5*exp(-0.15*s)/(1.05*s+1)
g2=1.5*exp(-0.05*s)/((s+1)*(0.15*s+1))
step(g0,g1,g2,1)
Note: It’s the initial
response that matters
for feedback control
(time from 0 to about 5*tauc)
g1
g0, g2
g0
g1, g2

## Slide 55: Simulation with control is as expected: Better performance with controller based on g2 (PID) than g1 (PI) but more input usage
g = 2*(15*s+1)/((20*s+1)*(s+1)*(0.1*s+1)^2)
gd=g
Using g1:
PI. tauc=0.15
Kc=(1/1.5)*1.05/(2*0.15)=2.33
taui=min(1.05,8*tauc)=1.05
taud=0
Using g2
PID. tauc=0.05
Kc=(1/1.5)*1.00/(2*0.05)=6.66
taui=min(1.05,8*tauc)=0.4
taud=0.15, tauf=0.015
y(t)
u(t)
y(t)
PI
PID
PI
PID

## Slide 56: Example: Approximation of zero for flow control
Note that so we get an overshoot in the step response
How should we approximate this as a first-order with delay model? It will depend on the value for tauc. If we apply the LHP-zero approximation rules then we get:
  Small tauc (tauc<9): (15s+1)/(9s+1) 15/9 (Rule T1) G(s)= k = 1.2*15/9 = 2
  Intermediate tauc (9<taux<15): (15s+1)/(9s+1) 15/tauc (Rule T1a) G(s)= k = 18/tauc
  Large tauc (tauc>15) . (15s+1)/(9s+1) 1 (Rule T1b) G(s)= k = 1.2
In all three cases we get so we get and in all three cases the SIMC PI-controller becomes a pure I-controller C(s)=KI/s where KI = 1/(k*tauc). Here tauc is free to choose.
Flow controller, The transfer function G0(s) is typical for a control valve where u=z=valve position and y=F =flow. Consider a typical valve equation . Following a step change in z, F will immediately jump (to 1.2*15/9=2), but then it will drop down again (to 1.2) because of the reduction in the pressure drop which for gases may take some time ( in this case). (See Exam 2022, Problem 5 for how to derive G0)
  For liquids the dynamics are fast because of small compressibility and can be neglected. Thus, for liquids we always have case 3 (tule T1b). However, the short-term flow overshoot may result in the phenomena of “water hammering”.
  For gases, also cases 1 or 2 may happen if the valve is close to a large gas holdup (large tank or large pipeline).
  For a flow controller, a typical value is tauc=10s.
  Some commercial controllers do not allow a pure I-controller. In this case, select taui as some small value (say taui=1s) and use Kc=KI*taui, that is, Kc=(1/k)*(taui/tauc) .
  However, if the dynamics for changing z or measuring F are slow compared to the desired closed-loop response time tauc, then a better approximatiom of the valve may be G=k/(tau1*s+1). In this case a PI-controller with tauc=tu1 is recommened (SIMC-rule).
Step in u at t=10
y(t)
Extra slide

## Slide 57: Shams’ method: Closed-loop setpoint response with P-controller with about 20-40% overshoot
Kc0=1.5
Δys=1
Δyu=0.54
Δyp=0.79
tp=4.4
Start from steady state and do step P-response
OBTAIN DATA IN RED (first overshoot
and undershoot), and then:
dyinf = 0.45*(dyp + dyu) % estimate dyinf (so don’t wait)
Mo =(dyp -dyinf)/dyinf % Mo=overshoot (about 0.3)
b=dyinf/dys % offset parameter
A = 1.152*Mo^2 - 1.607*Mo + 1.0
r = 2*A*abs(b/(1-b))
2. OBTAIN FIRST-ORDER with DELAY MODEL:
k = (1/Kc0) * abs(b/(1-b))
theta = tp*[0.309 + 0.209*exp(-0.61*r)]
tau = theta*r
3. CAN THEN USE SIMC PI-rule
Example 2: Get k=0.99, theta =1.67, tau=3.0
Ref: Shamssuzzoha and Skogestad (JPC, 2010) + modification by C. Grimholt (PID-book 2012)
Δy∞
Alternative to Ziegler-Nichols closed-loop experiment: Obtains more information and avoids cycling.